## Sheet1
run_name | usage_curve | controls_array | capacity_normOp | capacity_loadUp | V0 | T_cw | T_supply | T_storage | aqFrac_normalOp | aqFrac_loadUp | aqFrac_shed | defrost_factor
Required: Name that will specify html file title. | Required: Array of length of length 24 with hourly hot water usage in GPH. | Required: Array of length 24 with 'N' indicating normal operation, 'L' indicating load up, and 'S' indicating shed for each hour of the day. | Required: Capacity of HWPH when under normal operation in kBTU/hr. | Required: Capacity of HPWH when under load up operation in kBTU/hr. | Required: Total usable storage volume and volume of hot water at start of simulation in gallons. | Optional: Incoming city water temp in degrees F. Default: 50 | Optional: Supply temperature in degrees F. Default: 120 | Optional: Storage temperatrure in degrees F. Default: 150 | Optional: Aquastat fraction when HP is in normal mode. Value between 0 and 1. Default: 0.4 | Optional: Aquastat fraction when HP is in load up mode. Value between 0 and 1. Default: 0.2 | Optional: Aquastat fraction when HP is in shed mode. Value between 0 and 1. Default: 0.8 | Optional: Default: 1
market_3hr_24.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 108 | 120 | 1230
market_3hr_23.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 108 | 120 | 1190
market_3hr_22.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 117 | 130 | 1150
market_3hr_21.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 117 | 130 | 1100
market_3hr_20.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 126 | 140 | 1050
market_3hr_19.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 135 | 150 | 1000
market_3hr_18.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 144 | 160 | 930
market_3hr_17.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 153 | 170 | 860
market_3hr_16.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 162 | 180 | 780
market_3hr_15.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 171 | 190 | 690
market_3hr_14.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 180 | 200 | 590
market_3hr_13.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 198 | 220 | 490
market_3hr_12.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 216 | 240 | 410
market_3hr_11.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 234 | 260 | 330
market_3hr_10.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 252 | 280 | 270
market_3hr_9.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 288 | 320 | 210
market_3hr_24.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 108 | 120 | 1230
market_3hr_23.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 108 | 120 | 1190
market_3hr_22.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 117 | 130 | 1150
market_3hr_21.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 117 | 130 | 1100
market_3hr_20.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 126 | 140 | 1050
market_3hr_19.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 135 | 150 | 1000
market_3hr_18.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 144 | 160 | 930
market_3hr_17.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 153 | 170 | 860
market_3hr_16.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 162 | 180 | 780
market_3hr_15.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 171 | 190 | 690
market_3hr_14.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 180 | 200 | 590
market_3hr_13.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 198 | 220 | 490
market_3hr_12.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 216 | 240 | 410
market_3hr_11.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 234 | 260 | 330
market_3hr_10.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 252 | 280 | 270
market_3hr_9.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 288 | 320 | 210
market_3hr_24.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 108 | 120 | 1230
market_3hr_23.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 108 | 120 | 1190
market_3hr_22.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 117 | 130 | 1150
market_3hr_21.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 117 | 130 | 1100
market_3hr_20.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 126 | 140 | 1050
market_3hr_19.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 135 | 150 | 1000
market_3hr_18.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 144 | 160 | 930
market_3hr_17.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 153 | 170 | 860
market_3hr_16.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 162 | 180 | 780
market_3hr_15.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 171 | 190 | 690
market_3hr_14.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 180 | 200 | 590
market_3hr_13.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 198 | 220 | 490
market_3hr_12.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 216 | 240 | 410
market_3hr_11.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 234 | 260 | 330
market_3hr_10.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 252 | 280 | 270
market_3hr_9.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 288 | 320 | 210
market_3hr_24.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 108 | 120 | 1230
market_3hr_23.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 108 | 120 | 1190
market_3hr_22.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 117 | 130 | 1150
market_3hr_21.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 117 | 130 | 1100
market_3hr_20.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 126 | 140 | 1050
market_3hr_19.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 135 | 150 | 1000
market_3hr_18.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 144 | 160 | 930
market_3hr_17.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 153 | 170 | 860
market_3hr_16.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 162 | 180 | 780
market_3hr_15.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 171 | 190 | 690
market_3hr_14.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 180 | 200 | 590
market_3hr_13.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 198 | 220 | 490
market_3hr_12.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 216 | 240 | 410
market_3hr_11.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 234 | 260 | 330
market_3hr_10.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 252 | 280 | 270
market_3hr_9.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 288 | 320 | 210
market_3hr_24.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 108 | 120 | 1230
market_3hr_23.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 108 | 120 | 1190
market_3hr_22.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 117 | 130 | 1150
market_3hr_21.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 117 | 130 | 1100
market_3hr_20.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 126 | 140 | 1050
market_3hr_19.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 135 | 150 | 1000
market_3hr_18.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 144 | 160 | 930
market_3hr_17.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 153 | 170 | 860
market_3hr_16.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 162 | 180 | 780
market_3hr_15.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 171 | 190 | 690
market_3hr_14.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 180 | 200 | 590
market_3hr_13.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 198 | 220 | 490
market_3hr_12.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 216 | 240 | 410
market_3hr_11.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 234 | 260 | 330
market_3hr_10.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 252 | 280 | 270
market_3hr_9.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 288 | 320 | 210
market_3hr_24.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 108 | 120 | 1230
market_3hr_23.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 108 | 120 | 1190
market_3hr_22.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 117 | 130 | 1150
market_3hr_21.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 117 | 130 | 1100
market_3hr_20.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 126 | 140 | 1050
market_3hr_19.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 135 | 150 | 1000
market_3hr_18.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 144 | 160 | 930
market_3hr_17.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 153 | 170 | 860
market_3hr_16.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 162 | 180 | 780
market_3hr_15.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 171 | 190 | 690
market_3hr_14.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 180 | 200 | 590
market_3hr_13.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 198 | 220 | 490
market_3hr_12.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 216 | 240 | 410
market_3hr_11.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 234 | 260 | 330
market_3hr_10.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 252 | 280 | 270
market_3hr_9.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 288 | 320 | 210
market_peakRed_24.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 108 | 120 | 1230
market_peakRed_23.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 108 | 120 | 1190
market_peakRed_22.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 117 | 130 | 1150
market_peakRed_21.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 117 | 130 | 1100
market_peakRed_20.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 126 | 140 | 1050
market_peakRed_19.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 135 | 150 | 1000
market_peakRed_18.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 144 | 160 | 930
market_peakRed_17.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 153 | 170 | 860
market_peakRed_16.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 162 | 180 | 780
market_peakRed_15.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 171 | 190 | 690
market_peakRed_14.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 180 | 200 | 590
market_peakRed_13.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 198 | 220 | 490
market_peakRed_12.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 216 | 240 | 410
market_peakRed_11.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 234 | 260 | 330
market_peakRed_10.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 252 | 280 | 270
market_peakRed_9.0_25.0 | 54.71, 21.88, 10.94, 10.94, 10.94, 32.83, 273.56, 547.11, 361.09, 295.44, 76.6, 87.54, 76.6, 87.54, 43.77, 21.88, 32.83, 131.31, 196.96, 262.61, 317.33, 328.27, 229.79, 87.54 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 288 | 320 | 210
market_peakRed_24.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 108 | 120 | 1230
market_peakRed_23.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 108 | 120 | 1190
market_peakRed_22.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 117 | 130 | 1150
market_peakRed_21.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 117 | 130 | 1100
market_peakRed_20.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 126 | 140 | 1050
market_peakRed_19.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 135 | 150 | 1000
market_peakRed_18.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 144 | 160 | 930
market_peakRed_17.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 153 | 170 | 860
market_peakRed_16.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 162 | 180 | 780
market_peakRed_15.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 171 | 190 | 690
market_peakRed_14.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 180 | 200 | 590
market_peakRed_13.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 198 | 220 | 490
market_peakRed_12.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 216 | 240 | 410
market_peakRed_11.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 234 | 260 | 330
market_peakRed_10.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 252 | 280 | 270
market_peakRed_9.0_22.5 | 49.24, 19.7, 9.85, 9.85, 9.85, 29.54, 246.2, 492.4, 324.98, 265.9, 68.94, 78.78, 68.94, 78.78, 39.39, 19.7, 29.54, 118.18, 177.26, 236.35, 285.59, 295.44, 206.81, 78.78 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 288 | 320 | 210
market_peakRed_24.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 108 | 120 | 1230
market_peakRed_23.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 108 | 120 | 1190
market_peakRed_22.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 117 | 130 | 1150
market_peakRed_21.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 117 | 130 | 1100
market_peakRed_20.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 126 | 140 | 1050
market_peakRed_19.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 135 | 150 | 1000
market_peakRed_18.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 144 | 160 | 930
market_peakRed_17.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 153 | 170 | 860
market_peakRed_16.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 162 | 180 | 780
market_peakRed_15.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 171 | 190 | 690
market_peakRed_14.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 180 | 200 | 590
market_peakRed_13.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 198 | 220 | 490
market_peakRed_12.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 216 | 240 | 410
market_peakRed_11.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 234 | 260 | 330
market_peakRed_10.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 252 | 280 | 270
market_peakRed_9.0_20.0 | 43.77, 17.51, 8.75, 8.75, 8.75, 26.26, 218.84, 437.69, 288.88, 236.35, 61.28, 70.03, 61.28, 70.03, 35.02, 17.51, 26.26, 105.05, 157.57, 210.09, 253.86, 262.61, 183.83, 70.03 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 288 | 320 | 210
market_peakRed_24.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 108 | 120 | 1230
market_peakRed_23.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 108 | 120 | 1190
market_peakRed_22.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 117 | 130 | 1150
market_peakRed_21.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 117 | 130 | 1100
market_peakRed_20.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 126 | 140 | 1050
market_peakRed_19.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 135 | 150 | 1000
market_peakRed_18.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 144 | 160 | 930
market_peakRed_17.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 153 | 170 | 860
market_peakRed_16.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 162 | 180 | 780
market_peakRed_15.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 171 | 190 | 690
market_peakRed_14.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 180 | 200 | 590
market_peakRed_13.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 198 | 220 | 490
market_peakRed_12.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 216 | 240 | 410
market_peakRed_11.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 234 | 260 | 330
market_peakRed_10.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 252 | 280 | 270
market_peakRed_9.0_17.5 | 38.3, 15.32, 7.66, 7.66, 7.66, 22.98, 191.49, 382.98, 252.77, 206.81, 53.62, 61.28, 53.62, 61.28, 30.64, 15.32, 22.98, 91.91, 137.87, 183.83, 222.13, 229.79, 160.85, 61.28 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 288 | 320 | 210
market_peakRed_24.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 108 | 120 | 1230
market_peakRed_23.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 108 | 120 | 1190
market_peakRed_22.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 117 | 130 | 1150
market_peakRed_21.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 117 | 130 | 1100
market_peakRed_20.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 126 | 140 | 1050
market_peakRed_19.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 135 | 150 | 1000
market_peakRed_18.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 144 | 160 | 930
market_peakRed_17.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 153 | 170 | 860
market_peakRed_16.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 162 | 180 | 780
market_peakRed_15.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 171 | 190 | 690
market_peakRed_14.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 180 | 200 | 590
market_peakRed_13.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 198 | 220 | 490
market_peakRed_12.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 216 | 240 | 410
market_peakRed_11.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 234 | 260 | 330
market_peakRed_10.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 252 | 280 | 270
market_peakRed_9.0_15.0 | 32.83, 13.13, 6.57, 6.57, 6.57, 19.7, 164.13, 328.27, 216.66, 177.26, 45.96, 52.52, 45.96, 52.52, 26.26, 13.13, 19.7, 78.78, 118.18, 157.57, 190.4, 196.96, 137.87, 52.52 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 288 | 320 | 210
market_peakRed_24.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 108 | 120 | 1230
market_peakRed_23.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 108 | 120 | 1190
market_peakRed_22.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 117 | 130 | 1150
market_peakRed_21.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 117 | 130 | 1100
market_peakRed_20.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 126 | 140 | 1050
market_peakRed_19.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 135 | 150 | 1000
market_peakRed_18.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 144 | 160 | 930
market_peakRed_17.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 153 | 170 | 860
market_peakRed_16.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 162 | 180 | 780
market_peakRed_15.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 171 | 190 | 690
market_peakRed_14.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 180 | 200 | 590
market_peakRed_13.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 198 | 220 | 490
market_peakRed_12.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 216 | 240 | 410
market_peakRed_11.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 234 | 260 | 330
market_peakRed_10.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 252 | 280 | 270
market_peakRed_9.0_12.5 | 27.36, 10.94, 5.47, 5.47, 5.47, 16.41, 136.78, 273.56, 180.55, 147.72, 38.3, 43.77, 38.3, 43.77, 21.88, 10.94, 16.41, 65.65, 98.48, 131.31, 158.66, 164.13, 114.89, 43.77 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 288 | 320 | 210
lowIncome_3hr_24.0_25.0 | 147.3, 147.89, 46.4, 108.41, 67.61, 88.82, 142.0, 77.33, 150.69, 194.44, 299.46, 204.01, 221.98, 266.91, 170.57, 84.7, 205.34, 104.14, 147.15, 127.71, 204.75, 85.87, 119.46, 187.07 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 108 | 120 | 680
lowIncome_3hr_23.0_25.0 | 147.3, 147.89, 46.4, 108.41, 67.61, 88.82, 142.0, 77.33, 150.69, 194.44, 299.46, 204.01, 221.98, 266.91, 170.57, 84.7, 205.34, 104.14, 147.15, 127.71, 204.75, 85.87, 119.46, 187.07 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 117 | 130 | 610
lowIncome_3hr_22.0_25.0 | 147.3, 147.89, 46.4, 108.41, 67.61, 88.82, 142.0, 77.33, 150.69, 194.44, 299.46, 204.01, 221.98, 266.91, 170.57, 84.7, 205.34, 104.14, 147.15, 127.71, 204.75, 85.87, 119.46, 187.07 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 117 | 130 | 550
lowIncome_3hr_21.0_25.0 | 147.3, 147.89, 46.4, 108.41, 67.61, 88.82, 142.0, 77.33, 150.69, 194.44, 299.46, 204.01, 221.98, 266.91, 170.57, 84.7, 205.34, 104.14, 147.15, 127.71, 204.75, 85.87, 119.46, 187.07 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 126 | 140 | 480
lowIncome_3hr_20.0_25.0 | 147.3, 147.89, 46.4, 108.41, 67.61, 88.82, 142.0, 77.33, 150.69, 194.44, 299.46, 204.01, 221.98, 266.91, 170.57, 84.7, 205.34, 104.14, 147.15, 127.71, 204.75, 85.87, 119.46, 187.07 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 135 | 150 | 410
lowIncome_3hr_19.0_25.0 | 147.3, 147.89, 46.4, 108.41, 67.61, 88.82, 142.0, 77.33, 150.69, 194.44, 299.46, 204.01, 221.98, 266.91, 170.57, 84.7, 205.34, 104.14, 147.15, 127.71, 204.75, 85.87, 119.46, 187.07 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 144 | 160 | 340
lowIncome_3hr_18.0_25.0 | 147.3, 147.89, 46.4, 108.41, 67.61, 88.82, 142.0, 77.33, 150.69, 194.44, 299.46, 204.01, 221.98, 266.91, 170.57, 84.7, 205.34, 104.14, 147.15, 127.71, 204.75, 85.87, 119.46, 187.07 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 144 | 160 | 270
lowIncome_3hr_17.0_25.0 | 147.3, 147.89, 46.4, 108.41, 67.61, 88.82, 142.0, 77.33, 150.69, 194.44, 299.46, 204.01, 221.98, 266.91, 170.57, 84.7, 205.34, 104.14, 147.15, 127.71, 204.75, 85.87, 119.46, 187.07 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 153 | 170 | 200
lowIncome_3hr_16.0_25.0 | 147.3, 147.89, 46.4, 108.41, 67.61, 88.82, 142.0, 77.33, 150.69, 194.44, 299.46, 204.01, 221.98, 266.91, 170.57, 84.7, 205.34, 104.14, 147.15, 127.71, 204.75, 85.87, 119.46, 187.07 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 162 | 180 | 120
lowIncome_3hr_24.0_22.5 | 132.57, 133.1, 41.76, 97.57, 60.85, 79.94, 127.8, 69.6, 135.62, 174.99, 269.51, 183.61, 199.78, 240.22, 153.51, 76.23, 184.8, 93.73, 132.44, 114.94, 184.27, 77.29, 107.51, 168.36 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 108 | 120 | 680
lowIncome_3hr_23.0_22.5 | 132.57, 133.1, 41.76, 97.57, 60.85, 79.94, 127.8, 69.6, 135.62, 174.99, 269.51, 183.61, 199.78, 240.22, 153.51, 76.23, 184.8, 93.73, 132.44, 114.94, 184.27, 77.29, 107.51, 168.36 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 117 | 130 | 610
lowIncome_3hr_22.0_22.5 | 132.57, 133.1, 41.76, 97.57, 60.85, 79.94, 127.8, 69.6, 135.62, 174.99, 269.51, 183.61, 199.78, 240.22, 153.51, 76.23, 184.8, 93.73, 132.44, 114.94, 184.27, 77.29, 107.51, 168.36 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 117 | 130 | 550
lowIncome_3hr_21.0_22.5 | 132.57, 133.1, 41.76, 97.57, 60.85, 79.94, 127.8, 69.6, 135.62, 174.99, 269.51, 183.61, 199.78, 240.22, 153.51, 76.23, 184.8, 93.73, 132.44, 114.94, 184.27, 77.29, 107.51, 168.36 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 126 | 140 | 480
lowIncome_3hr_20.0_22.5 | 132.57, 133.1, 41.76, 97.57, 60.85, 79.94, 127.8, 69.6, 135.62, 174.99, 269.51, 183.61, 199.78, 240.22, 153.51, 76.23, 184.8, 93.73, 132.44, 114.94, 184.27, 77.29, 107.51, 168.36 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 135 | 150 | 410
lowIncome_3hr_19.0_22.5 | 132.57, 133.1, 41.76, 97.57, 60.85, 79.94, 127.8, 69.6, 135.62, 174.99, 269.51, 183.61, 199.78, 240.22, 153.51, 76.23, 184.8, 93.73, 132.44, 114.94, 184.27, 77.29, 107.51, 168.36 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 144 | 160 | 340
lowIncome_3hr_18.0_22.5 | 132.57, 133.1, 41.76, 97.57, 60.85, 79.94, 127.8, 69.6, 135.62, 174.99, 269.51, 183.61, 199.78, 240.22, 153.51, 76.23, 184.8, 93.73, 132.44, 114.94, 184.27, 77.29, 107.51, 168.36 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 144 | 160 | 270
lowIncome_3hr_17.0_22.5 | 132.57, 133.1, 41.76, 97.57, 60.85, 79.94, 127.8, 69.6, 135.62, 174.99, 269.51, 183.61, 199.78, 240.22, 153.51, 76.23, 184.8, 93.73, 132.44, 114.94, 184.27, 77.29, 107.51, 168.36 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 153 | 170 | 200
lowIncome_3hr_16.0_22.5 | 132.57, 133.1, 41.76, 97.57, 60.85, 79.94, 127.8, 69.6, 135.62, 174.99, 269.51, 183.61, 199.78, 240.22, 153.51, 76.23, 184.8, 93.73, 132.44, 114.94, 184.27, 77.29, 107.51, 168.36 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 162 | 180 | 120
lowIncome_3hr_24.0_20.0 | 117.84, 118.31, 37.12, 86.73, 54.09, 71.06, 113.6, 61.87, 120.55, 155.55, 239.57, 163.21, 177.58, 213.53, 136.46, 67.76, 164.27, 83.31, 117.72, 102.17, 163.8, 68.7, 95.57, 149.66 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 108 | 120 | 680
lowIncome_3hr_23.0_20.0 | 117.84, 118.31, 37.12, 86.73, 54.09, 71.06, 113.6, 61.87, 120.55, 155.55, 239.57, 163.21, 177.58, 213.53, 136.46, 67.76, 164.27, 83.31, 117.72, 102.17, 163.8, 68.7, 95.57, 149.66 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 117 | 130 | 610
lowIncome_3hr_22.0_20.0 | 117.84, 118.31, 37.12, 86.73, 54.09, 71.06, 113.6, 61.87, 120.55, 155.55, 239.57, 163.21, 177.58, 213.53, 136.46, 67.76, 164.27, 83.31, 117.72, 102.17, 163.8, 68.7, 95.57, 149.66 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 117 | 130 | 550
lowIncome_3hr_21.0_20.0 | 117.84, 118.31, 37.12, 86.73, 54.09, 71.06, 113.6, 61.87, 120.55, 155.55, 239.57, 163.21, 177.58, 213.53, 136.46, 67.76, 164.27, 83.31, 117.72, 102.17, 163.8, 68.7, 95.57, 149.66 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 126 | 140 | 480
lowIncome_3hr_20.0_20.0 | 117.84, 118.31, 37.12, 86.73, 54.09, 71.06, 113.6, 61.87, 120.55, 155.55, 239.57, 163.21, 177.58, 213.53, 136.46, 67.76, 164.27, 83.31, 117.72, 102.17, 163.8, 68.7, 95.57, 149.66 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 135 | 150 | 410
lowIncome_3hr_19.0_20.0 | 117.84, 118.31, 37.12, 86.73, 54.09, 71.06, 113.6, 61.87, 120.55, 155.55, 239.57, 163.21, 177.58, 213.53, 136.46, 67.76, 164.27, 83.31, 117.72, 102.17, 163.8, 68.7, 95.57, 149.66 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 144 | 160 | 340
lowIncome_3hr_18.0_20.0 | 117.84, 118.31, 37.12, 86.73, 54.09, 71.06, 113.6, 61.87, 120.55, 155.55, 239.57, 163.21, 177.58, 213.53, 136.46, 67.76, 164.27, 83.31, 117.72, 102.17, 163.8, 68.7, 95.57, 149.66 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 144 | 160 | 270
lowIncome_3hr_17.0_20.0 | 117.84, 118.31, 37.12, 86.73, 54.09, 71.06, 113.6, 61.87, 120.55, 155.55, 239.57, 163.21, 177.58, 213.53, 136.46, 67.76, 164.27, 83.31, 117.72, 102.17, 163.8, 68.7, 95.57, 149.66 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 153 | 170 | 200
lowIncome_3hr_16.0_20.0 | 117.84, 118.31, 37.12, 86.73, 54.09, 71.06, 113.6, 61.87, 120.55, 155.55, 239.57, 163.21, 177.58, 213.53, 136.46, 67.76, 164.27, 83.31, 117.72, 102.17, 163.8, 68.7, 95.57, 149.66 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 162 | 180 | 120
lowIncome_3hr_24.0_17.5 | 103.11, 103.52, 32.48, 75.89, 47.33, 62.18, 99.4, 54.13, 105.48, 136.11, 209.62, 142.81, 155.39, 186.84, 119.4, 59.29, 143.74, 72.9, 103.01, 89.4, 143.32, 60.11, 83.62, 130.95 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 108 | 120 | 680
lowIncome_3hr_23.0_17.5 | 103.11, 103.52, 32.48, 75.89, 47.33, 62.18, 99.4, 54.13, 105.48, 136.11, 209.62, 142.81, 155.39, 186.84, 119.4, 59.29, 143.74, 72.9, 103.01, 89.4, 143.32, 60.11, 83.62, 130.95 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 117 | 130 | 610
lowIncome_3hr_22.0_17.5 | 103.11, 103.52, 32.48, 75.89, 47.33, 62.18, 99.4, 54.13, 105.48, 136.11, 209.62, 142.81, 155.39, 186.84, 119.4, 59.29, 143.74, 72.9, 103.01, 89.4, 143.32, 60.11, 83.62, 130.95 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 117 | 130 | 550
lowIncome_3hr_21.0_17.5 | 103.11, 103.52, 32.48, 75.89, 47.33, 62.18, 99.4, 54.13, 105.48, 136.11, 209.62, 142.81, 155.39, 186.84, 119.4, 59.29, 143.74, 72.9, 103.01, 89.4, 143.32, 60.11, 83.62, 130.95 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 126 | 140 | 480
lowIncome_3hr_20.0_17.5 | 103.11, 103.52, 32.48, 75.89, 47.33, 62.18, 99.4, 54.13, 105.48, 136.11, 209.62, 142.81, 155.39, 186.84, 119.4, 59.29, 143.74, 72.9, 103.01, 89.4, 143.32, 60.11, 83.62, 130.95 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 135 | 150 | 410
lowIncome_3hr_19.0_17.5 | 103.11, 103.52, 32.48, 75.89, 47.33, 62.18, 99.4, 54.13, 105.48, 136.11, 209.62, 142.81, 155.39, 186.84, 119.4, 59.29, 143.74, 72.9, 103.01, 89.4, 143.32, 60.11, 83.62, 130.95 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 144 | 160 | 340
lowIncome_3hr_18.0_17.5 | 103.11, 103.52, 32.48, 75.89, 47.33, 62.18, 99.4, 54.13, 105.48, 136.11, 209.62, 142.81, 155.39, 186.84, 119.4, 59.29, 143.74, 72.9, 103.01, 89.4, 143.32, 60.11, 83.62, 130.95 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 144 | 160 | 270
lowIncome_3hr_17.0_17.5 | 103.11, 103.52, 32.48, 75.89, 47.33, 62.18, 99.4, 54.13, 105.48, 136.11, 209.62, 142.81, 155.39, 186.84, 119.4, 59.29, 143.74, 72.9, 103.01, 89.4, 143.32, 60.11, 83.62, 130.95 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 153 | 170 | 200
lowIncome_3hr_16.0_17.5 | 103.11, 103.52, 32.48, 75.89, 47.33, 62.18, 99.4, 54.13, 105.48, 136.11, 209.62, 142.81, 155.39, 186.84, 119.4, 59.29, 143.74, 72.9, 103.01, 89.4, 143.32, 60.11, 83.62, 130.95 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 162 | 180 | 120
lowIncome_3hr_24.0_15.0 | 88.38, 88.73, 27.84, 65.05, 40.57, 53.29, 85.2, 46.4, 90.41, 116.66, 179.68, 122.41, 133.19, 160.14, 102.34, 50.82, 123.2, 62.48, 88.29, 76.63, 122.85, 51.52, 71.68, 112.24 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 108 | 120 | 680
lowIncome_3hr_23.0_15.0 | 88.38, 88.73, 27.84, 65.05, 40.57, 53.29, 85.2, 46.4, 90.41, 116.66, 179.68, 122.41, 133.19, 160.14, 102.34, 50.82, 123.2, 62.48, 88.29, 76.63, 122.85, 51.52, 71.68, 112.24 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 117 | 130 | 610
lowIncome_3hr_22.0_15.0 | 88.38, 88.73, 27.84, 65.05, 40.57, 53.29, 85.2, 46.4, 90.41, 116.66, 179.68, 122.41, 133.19, 160.14, 102.34, 50.82, 123.2, 62.48, 88.29, 76.63, 122.85, 51.52, 71.68, 112.24 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 117 | 130 | 550
lowIncome_3hr_21.0_15.0 | 88.38, 88.73, 27.84, 65.05, 40.57, 53.29, 85.2, 46.4, 90.41, 116.66, 179.68, 122.41, 133.19, 160.14, 102.34, 50.82, 123.2, 62.48, 88.29, 76.63, 122.85, 51.52, 71.68, 112.24 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 126 | 140 | 480
lowIncome_3hr_20.0_15.0 | 88.38, 88.73, 27.84, 65.05, 40.57, 53.29, 85.2, 46.4, 90.41, 116.66, 179.68, 122.41, 133.19, 160.14, 102.34, 50.82, 123.2, 62.48, 88.29, 76.63, 122.85, 51.52, 71.68, 112.24 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 135 | 150 | 410
lowIncome_3hr_19.0_15.0 | 88.38, 88.73, 27.84, 65.05, 40.57, 53.29, 85.2, 46.4, 90.41, 116.66, 179.68, 122.41, 133.19, 160.14, 102.34, 50.82, 123.2, 62.48, 88.29, 76.63, 122.85, 51.52, 71.68, 112.24 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 144 | 160 | 340
lowIncome_3hr_18.0_15.0 | 88.38, 88.73, 27.84, 65.05, 40.57, 53.29, 85.2, 46.4, 90.41, 116.66, 179.68, 122.41, 133.19, 160.14, 102.34, 50.82, 123.2, 62.48, 88.29, 76.63, 122.85, 51.52, 71.68, 112.24 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 144 | 160 | 270
lowIncome_3hr_17.0_15.0 | 88.38, 88.73, 27.84, 65.05, 40.57, 53.29, 85.2, 46.4, 90.41, 116.66, 179.68, 122.41, 133.19, 160.14, 102.34, 50.82, 123.2, 62.48, 88.29, 76.63, 122.85, 51.52, 71.68, 112.24 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 153 | 170 | 200
lowIncome_3hr_16.0_15.0 | 88.38, 88.73, 27.84, 65.05, 40.57, 53.29, 85.2, 46.4, 90.41, 116.66, 179.68, 122.41, 133.19, 160.14, 102.34, 50.82, 123.2, 62.48, 88.29, 76.63, 122.85, 51.52, 71.68, 112.24 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 162 | 180 | 120
lowIncome_3hr_24.0_12.5 | 73.65, 73.94, 23.2, 54.21, 33.81, 44.41, 71.0, 38.67, 75.34, 97.22, 149.73, 102.0, 110.99, 133.45, 85.29, 42.35, 102.67, 52.07, 73.58, 63.86, 102.37, 42.94, 59.73, 93.54 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 108 | 120 | 680
lowIncome_3hr_23.0_12.5 | 73.65, 73.94, 23.2, 54.21, 33.81, 44.41, 71.0, 38.67, 75.34, 97.22, 149.73, 102.0, 110.99, 133.45, 85.29, 42.35, 102.67, 52.07, 73.58, 63.86, 102.37, 42.94, 59.73, 93.54 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 117 | 130 | 610
lowIncome_3hr_22.0_12.5 | 73.65, 73.94, 23.2, 54.21, 33.81, 44.41, 71.0, 38.67, 75.34, 97.22, 149.73, 102.0, 110.99, 133.45, 85.29, 42.35, 102.67, 52.07, 73.58, 63.86, 102.37, 42.94, 59.73, 93.54 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 117 | 130 | 550
lowIncome_3hr_21.0_12.5 | 73.65, 73.94, 23.2, 54.21, 33.81, 44.41, 71.0, 38.67, 75.34, 97.22, 149.73, 102.0, 110.99, 133.45, 85.29, 42.35, 102.67, 52.07, 73.58, 63.86, 102.37, 42.94, 59.73, 93.54 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 126 | 140 | 480
lowIncome_3hr_20.0_12.5 | 73.65, 73.94, 23.2, 54.21, 33.81, 44.41, 71.0, 38.67, 75.34, 97.22, 149.73, 102.0, 110.99, 133.45, 85.29, 42.35, 102.67, 52.07, 73.58, 63.86, 102.37, 42.94, 59.73, 93.54 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 135 | 150 | 410
lowIncome_3hr_19.0_12.5 | 73.65, 73.94, 23.2, 54.21, 33.81, 44.41, 71.0, 38.67, 75.34, 97.22, 149.73, 102.0, 110.99, 133.45, 85.29, 42.35, 102.67, 52.07, 73.58, 63.86, 102.37, 42.94, 59.73, 93.54 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 144 | 160 | 340
lowIncome_3hr_18.0_12.5 | 73.65, 73.94, 23.2, 54.21, 33.81, 44.41, 71.0, 38.67, 75.34, 97.22, 149.73, 102.0, 110.99, 133.45, 85.29, 42.35, 102.67, 52.07, 73.58, 63.86, 102.37, 42.94, 59.73, 93.54 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 144 | 160 | 270
lowIncome_3hr_17.0_12.5 | 73.65, 73.94, 23.2, 54.21, 33.81, 44.41, 71.0, 38.67, 75.34, 97.22, 149.73, 102.0, 110.99, 133.45, 85.29, 42.35, 102.67, 52.07, 73.58, 63.86, 102.37, 42.94, 59.73, 93.54 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 153 | 170 | 200
lowIncome_3hr_16.0_12.5 | 73.65, 73.94, 23.2, 54.21, 33.81, 44.41, 71.0, 38.67, 75.34, 97.22, 149.73, 102.0, 110.99, 133.45, 85.29, 42.35, 102.67, 52.07, 73.58, 63.86, 102.37, 42.94, 59.73, 93.54 | N, N, N, N, L, L, S, S, S, N, L, L, L, L, L, L, L, S, S, S, N, N, N, N | 162 | 180 | 120
lowIncome_peakRed_24.0_25.0 | 147.3, 147.89, 46.4, 108.41, 67.61, 88.82, 142.0, 77.33, 150.69, 194.44, 299.46, 204.01, 221.98, 266.91, 170.57, 84.7, 205.34, 104.14, 147.15, 127.71, 204.75, 85.87, 119.46, 187.07 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 108 | 120 | 680
lowIncome_peakRed_23.0_25.0 | 147.3, 147.89, 46.4, 108.41, 67.61, 88.82, 142.0, 77.33, 150.69, 194.44, 299.46, 204.01, 221.98, 266.91, 170.57, 84.7, 205.34, 104.14, 147.15, 127.71, 204.75, 85.87, 119.46, 187.07 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 117 | 130 | 610
lowIncome_peakRed_22.0_25.0 | 147.3, 147.89, 46.4, 108.41, 67.61, 88.82, 142.0, 77.33, 150.69, 194.44, 299.46, 204.01, 221.98, 266.91, 170.57, 84.7, 205.34, 104.14, 147.15, 127.71, 204.75, 85.87, 119.46, 187.07 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 117 | 130 | 550
lowIncome_peakRed_21.0_25.0 | 147.3, 147.89, 46.4, 108.41, 67.61, 88.82, 142.0, 77.33, 150.69, 194.44, 299.46, 204.01, 221.98, 266.91, 170.57, 84.7, 205.34, 104.14, 147.15, 127.71, 204.75, 85.87, 119.46, 187.07 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 126 | 140 | 480
lowIncome_peakRed_20.0_25.0 | 147.3, 147.89, 46.4, 108.41, 67.61, 88.82, 142.0, 77.33, 150.69, 194.44, 299.46, 204.01, 221.98, 266.91, 170.57, 84.7, 205.34, 104.14, 147.15, 127.71, 204.75, 85.87, 119.46, 187.07 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 135 | 150 | 410
lowIncome_peakRed_19.0_25.0 | 147.3, 147.89, 46.4, 108.41, 67.61, 88.82, 142.0, 77.33, 150.69, 194.44, 299.46, 204.01, 221.98, 266.91, 170.57, 84.7, 205.34, 104.14, 147.15, 127.71, 204.75, 85.87, 119.46, 187.07 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 144 | 160 | 340
lowIncome_peakRed_18.0_25.0 | 147.3, 147.89, 46.4, 108.41, 67.61, 88.82, 142.0, 77.33, 150.69, 194.44, 299.46, 204.01, 221.98, 266.91, 170.57, 84.7, 205.34, 104.14, 147.15, 127.71, 204.75, 85.87, 119.46, 187.07 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 144 | 160 | 270
lowIncome_peakRed_17.0_25.0 | 147.3, 147.89, 46.4, 108.41, 67.61, 88.82, 142.0, 77.33, 150.69, 194.44, 299.46, 204.01, 221.98, 266.91, 170.57, 84.7, 205.34, 104.14, 147.15, 127.71, 204.75, 85.87, 119.46, 187.07 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 153 | 170 | 200
lowIncome_peakRed_16.0_25.0 | 147.3, 147.89, 46.4, 108.41, 67.61, 88.82, 142.0, 77.33, 150.69, 194.44, 299.46, 204.01, 221.98, 266.91, 170.57, 84.7, 205.34, 104.14, 147.15, 127.71, 204.75, 85.87, 119.46, 187.07 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 162 | 180 | 120
lowIncome_peakRed_24.0_22.5 | 132.57, 133.1, 41.76, 97.57, 60.85, 79.94, 127.8, 69.6, 135.62, 174.99, 269.51, 183.61, 199.78, 240.22, 153.51, 76.23, 184.8, 93.73, 132.44, 114.94, 184.27, 77.29, 107.51, 168.36 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 108 | 120 | 680
lowIncome_peakRed_23.0_22.5 | 132.57, 133.1, 41.76, 97.57, 60.85, 79.94, 127.8, 69.6, 135.62, 174.99, 269.51, 183.61, 199.78, 240.22, 153.51, 76.23, 184.8, 93.73, 132.44, 114.94, 184.27, 77.29, 107.51, 168.36 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 117 | 130 | 610
lowIncome_peakRed_22.0_22.5 | 132.57, 133.1, 41.76, 97.57, 60.85, 79.94, 127.8, 69.6, 135.62, 174.99, 269.51, 183.61, 199.78, 240.22, 153.51, 76.23, 184.8, 93.73, 132.44, 114.94, 184.27, 77.29, 107.51, 168.36 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 117 | 130 | 550
lowIncome_peakRed_21.0_22.5 | 132.57, 133.1, 41.76, 97.57, 60.85, 79.94, 127.8, 69.6, 135.62, 174.99, 269.51, 183.61, 199.78, 240.22, 153.51, 76.23, 184.8, 93.73, 132.44, 114.94, 184.27, 77.29, 107.51, 168.36 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 126 | 140 | 480
lowIncome_peakRed_20.0_22.5 | 132.57, 133.1, 41.76, 97.57, 60.85, 79.94, 127.8, 69.6, 135.62, 174.99, 269.51, 183.61, 199.78, 240.22, 153.51, 76.23, 184.8, 93.73, 132.44, 114.94, 184.27, 77.29, 107.51, 168.36 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 135 | 150 | 410
lowIncome_peakRed_19.0_22.5 | 132.57, 133.1, 41.76, 97.57, 60.85, 79.94, 127.8, 69.6, 135.62, 174.99, 269.51, 183.61, 199.78, 240.22, 153.51, 76.23, 184.8, 93.73, 132.44, 114.94, 184.27, 77.29, 107.51, 168.36 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 144 | 160 | 340
lowIncome_peakRed_18.0_22.5 | 132.57, 133.1, 41.76, 97.57, 60.85, 79.94, 127.8, 69.6, 135.62, 174.99, 269.51, 183.61, 199.78, 240.22, 153.51, 76.23, 184.8, 93.73, 132.44, 114.94, 184.27, 77.29, 107.51, 168.36 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 144 | 160 | 270
lowIncome_peakRed_17.0_22.5 | 132.57, 133.1, 41.76, 97.57, 60.85, 79.94, 127.8, 69.6, 135.62, 174.99, 269.51, 183.61, 199.78, 240.22, 153.51, 76.23, 184.8, 93.73, 132.44, 114.94, 184.27, 77.29, 107.51, 168.36 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 153 | 170 | 200
lowIncome_peakRed_16.0_22.5 | 132.57, 133.1, 41.76, 97.57, 60.85, 79.94, 127.8, 69.6, 135.62, 174.99, 269.51, 183.61, 199.78, 240.22, 153.51, 76.23, 184.8, 93.73, 132.44, 114.94, 184.27, 77.29, 107.51, 168.36 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 162 | 180 | 120
lowIncome_peakRed_24.0_20.0 | 117.84, 118.31, 37.12, 86.73, 54.09, 71.06, 113.6, 61.87, 120.55, 155.55, 239.57, 163.21, 177.58, 213.53, 136.46, 67.76, 164.27, 83.31, 117.72, 102.17, 163.8, 68.7, 95.57, 149.66 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 108 | 120 | 680
lowIncome_peakRed_23.0_20.0 | 117.84, 118.31, 37.12, 86.73, 54.09, 71.06, 113.6, 61.87, 120.55, 155.55, 239.57, 163.21, 177.58, 213.53, 136.46, 67.76, 164.27, 83.31, 117.72, 102.17, 163.8, 68.7, 95.57, 149.66 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 117 | 130 | 610
lowIncome_peakRed_22.0_20.0 | 117.84, 118.31, 37.12, 86.73, 54.09, 71.06, 113.6, 61.87, 120.55, 155.55, 239.57, 163.21, 177.58, 213.53, 136.46, 67.76, 164.27, 83.31, 117.72, 102.17, 163.8, 68.7, 95.57, 149.66 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 117 | 130 | 550
lowIncome_peakRed_21.0_20.0 | 117.84, 118.31, 37.12, 86.73, 54.09, 71.06, 113.6, 61.87, 120.55, 155.55, 239.57, 163.21, 177.58, 213.53, 136.46, 67.76, 164.27, 83.31, 117.72, 102.17, 163.8, 68.7, 95.57, 149.66 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 126 | 140 | 480
lowIncome_peakRed_20.0_20.0 | 117.84, 118.31, 37.12, 86.73, 54.09, 71.06, 113.6, 61.87, 120.55, 155.55, 239.57, 163.21, 177.58, 213.53, 136.46, 67.76, 164.27, 83.31, 117.72, 102.17, 163.8, 68.7, 95.57, 149.66 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 135 | 150 | 410
lowIncome_peakRed_19.0_20.0 | 117.84, 118.31, 37.12, 86.73, 54.09, 71.06, 113.6, 61.87, 120.55, 155.55, 239.57, 163.21, 177.58, 213.53, 136.46, 67.76, 164.27, 83.31, 117.72, 102.17, 163.8, 68.7, 95.57, 149.66 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 144 | 160 | 340
lowIncome_peakRed_18.0_20.0 | 117.84, 118.31, 37.12, 86.73, 54.09, 71.06, 113.6, 61.87, 120.55, 155.55, 239.57, 163.21, 177.58, 213.53, 136.46, 67.76, 164.27, 83.31, 117.72, 102.17, 163.8, 68.7, 95.57, 149.66 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 144 | 160 | 270
lowIncome_peakRed_17.0_20.0 | 117.84, 118.31, 37.12, 86.73, 54.09, 71.06, 113.6, 61.87, 120.55, 155.55, 239.57, 163.21, 177.58, 213.53, 136.46, 67.76, 164.27, 83.31, 117.72, 102.17, 163.8, 68.7, 95.57, 149.66 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 153 | 170 | 200
lowIncome_peakRed_16.0_20.0 | 117.84, 118.31, 37.12, 86.73, 54.09, 71.06, 113.6, 61.87, 120.55, 155.55, 239.57, 163.21, 177.58, 213.53, 136.46, 67.76, 164.27, 83.31, 117.72, 102.17, 163.8, 68.7, 95.57, 149.66 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 162 | 180 | 120
lowIncome_peakRed_24.0_17.5 | 103.11, 103.52, 32.48, 75.89, 47.33, 62.18, 99.4, 54.13, 105.48, 136.11, 209.62, 142.81, 155.39, 186.84, 119.4, 59.29, 143.74, 72.9, 103.01, 89.4, 143.32, 60.11, 83.62, 130.95 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 108 | 120 | 680
lowIncome_peakRed_23.0_17.5 | 103.11, 103.52, 32.48, 75.89, 47.33, 62.18, 99.4, 54.13, 105.48, 136.11, 209.62, 142.81, 155.39, 186.84, 119.4, 59.29, 143.74, 72.9, 103.01, 89.4, 143.32, 60.11, 83.62, 130.95 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 117 | 130 | 610
lowIncome_peakRed_22.0_17.5 | 103.11, 103.52, 32.48, 75.89, 47.33, 62.18, 99.4, 54.13, 105.48, 136.11, 209.62, 142.81, 155.39, 186.84, 119.4, 59.29, 143.74, 72.9, 103.01, 89.4, 143.32, 60.11, 83.62, 130.95 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 117 | 130 | 550
lowIncome_peakRed_21.0_17.5 | 103.11, 103.52, 32.48, 75.89, 47.33, 62.18, 99.4, 54.13, 105.48, 136.11, 209.62, 142.81, 155.39, 186.84, 119.4, 59.29, 143.74, 72.9, 103.01, 89.4, 143.32, 60.11, 83.62, 130.95 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 126 | 140 | 480
lowIncome_peakRed_20.0_17.5 | 103.11, 103.52, 32.48, 75.89, 47.33, 62.18, 99.4, 54.13, 105.48, 136.11, 209.62, 142.81, 155.39, 186.84, 119.4, 59.29, 143.74, 72.9, 103.01, 89.4, 143.32, 60.11, 83.62, 130.95 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 135 | 150 | 410
lowIncome_peakRed_19.0_17.5 | 103.11, 103.52, 32.48, 75.89, 47.33, 62.18, 99.4, 54.13, 105.48, 136.11, 209.62, 142.81, 155.39, 186.84, 119.4, 59.29, 143.74, 72.9, 103.01, 89.4, 143.32, 60.11, 83.62, 130.95 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 144 | 160 | 340
lowIncome_peakRed_18.0_17.5 | 103.11, 103.52, 32.48, 75.89, 47.33, 62.18, 99.4, 54.13, 105.48, 136.11, 209.62, 142.81, 155.39, 186.84, 119.4, 59.29, 143.74, 72.9, 103.01, 89.4, 143.32, 60.11, 83.62, 130.95 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 144 | 160 | 270
lowIncome_peakRed_17.0_17.5 | 103.11, 103.52, 32.48, 75.89, 47.33, 62.18, 99.4, 54.13, 105.48, 136.11, 209.62, 142.81, 155.39, 186.84, 119.4, 59.29, 143.74, 72.9, 103.01, 89.4, 143.32, 60.11, 83.62, 130.95 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 153 | 170 | 200
lowIncome_peakRed_16.0_17.5 | 103.11, 103.52, 32.48, 75.89, 47.33, 62.18, 99.4, 54.13, 105.48, 136.11, 209.62, 142.81, 155.39, 186.84, 119.4, 59.29, 143.74, 72.9, 103.01, 89.4, 143.32, 60.11, 83.62, 130.95 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 162 | 180 | 120
lowIncome_peakRed_24.0_15.0 | 88.38, 88.73, 27.84, 65.05, 40.57, 53.29, 85.2, 46.4, 90.41, 116.66, 179.68, 122.41, 133.19, 160.14, 102.34, 50.82, 123.2, 62.48, 88.29, 76.63, 122.85, 51.52, 71.68, 112.24 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 108 | 120 | 680
lowIncome_peakRed_23.0_15.0 | 88.38, 88.73, 27.84, 65.05, 40.57, 53.29, 85.2, 46.4, 90.41, 116.66, 179.68, 122.41, 133.19, 160.14, 102.34, 50.82, 123.2, 62.48, 88.29, 76.63, 122.85, 51.52, 71.68, 112.24 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 117 | 130 | 610
lowIncome_peakRed_22.0_15.0 | 88.38, 88.73, 27.84, 65.05, 40.57, 53.29, 85.2, 46.4, 90.41, 116.66, 179.68, 122.41, 133.19, 160.14, 102.34, 50.82, 123.2, 62.48, 88.29, 76.63, 122.85, 51.52, 71.68, 112.24 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 117 | 130 | 550
lowIncome_peakRed_21.0_15.0 | 88.38, 88.73, 27.84, 65.05, 40.57, 53.29, 85.2, 46.4, 90.41, 116.66, 179.68, 122.41, 133.19, 160.14, 102.34, 50.82, 123.2, 62.48, 88.29, 76.63, 122.85, 51.52, 71.68, 112.24 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 126 | 140 | 480
lowIncome_peakRed_20.0_15.0 | 88.38, 88.73, 27.84, 65.05, 40.57, 53.29, 85.2, 46.4, 90.41, 116.66, 179.68, 122.41, 133.19, 160.14, 102.34, 50.82, 123.2, 62.48, 88.29, 76.63, 122.85, 51.52, 71.68, 112.24 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 135 | 150 | 410
lowIncome_peakRed_19.0_15.0 | 88.38, 88.73, 27.84, 65.05, 40.57, 53.29, 85.2, 46.4, 90.41, 116.66, 179.68, 122.41, 133.19, 160.14, 102.34, 50.82, 123.2, 62.48, 88.29, 76.63, 122.85, 51.52, 71.68, 112.24 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 144 | 160 | 340
lowIncome_peakRed_18.0_15.0 | 88.38, 88.73, 27.84, 65.05, 40.57, 53.29, 85.2, 46.4, 90.41, 116.66, 179.68, 122.41, 133.19, 160.14, 102.34, 50.82, 123.2, 62.48, 88.29, 76.63, 122.85, 51.52, 71.68, 112.24 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 144 | 160 | 270
lowIncome_peakRed_17.0_15.0 | 88.38, 88.73, 27.84, 65.05, 40.57, 53.29, 85.2, 46.4, 90.41, 116.66, 179.68, 122.41, 133.19, 160.14, 102.34, 50.82, 123.2, 62.48, 88.29, 76.63, 122.85, 51.52, 71.68, 112.24 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 153 | 170 | 200
lowIncome_peakRed_16.0_15.0 | 88.38, 88.73, 27.84, 65.05, 40.57, 53.29, 85.2, 46.4, 90.41, 116.66, 179.68, 122.41, 133.19, 160.14, 102.34, 50.82, 123.2, 62.48, 88.29, 76.63, 122.85, 51.52, 71.68, 112.24 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 162 | 180 | 120
lowIncome_peakRed_24.0_12.5 | 73.65, 73.94, 23.2, 54.21, 33.81, 44.41, 71.0, 38.67, 75.34, 97.22, 149.73, 102.0, 110.99, 133.45, 85.29, 42.35, 102.67, 52.07, 73.58, 63.86, 102.37, 42.94, 59.73, 93.54 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 108 | 120 | 680
lowIncome_peakRed_23.0_12.5 | 73.65, 73.94, 23.2, 54.21, 33.81, 44.41, 71.0, 38.67, 75.34, 97.22, 149.73, 102.0, 110.99, 133.45, 85.29, 42.35, 102.67, 52.07, 73.58, 63.86, 102.37, 42.94, 59.73, 93.54 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 117 | 130 | 610
lowIncome_peakRed_22.0_12.5 | 73.65, 73.94, 23.2, 54.21, 33.81, 44.41, 71.0, 38.67, 75.34, 97.22, 149.73, 102.0, 110.99, 133.45, 85.29, 42.35, 102.67, 52.07, 73.58, 63.86, 102.37, 42.94, 59.73, 93.54 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 117 | 130 | 550
lowIncome_peakRed_21.0_12.5 | 73.65, 73.94, 23.2, 54.21, 33.81, 44.41, 71.0, 38.67, 75.34, 97.22, 149.73, 102.0, 110.99, 133.45, 85.29, 42.35, 102.67, 52.07, 73.58, 63.86, 102.37, 42.94, 59.73, 93.54 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 126 | 140 | 480
lowIncome_peakRed_20.0_12.5 | 73.65, 73.94, 23.2, 54.21, 33.81, 44.41, 71.0, 38.67, 75.34, 97.22, 149.73, 102.0, 110.99, 133.45, 85.29, 42.35, 102.67, 52.07, 73.58, 63.86, 102.37, 42.94, 59.73, 93.54 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 135 | 150 | 410
lowIncome_peakRed_19.0_12.5 | 73.65, 73.94, 23.2, 54.21, 33.81, 44.41, 71.0, 38.67, 75.34, 97.22, 149.73, 102.0, 110.99, 133.45, 85.29, 42.35, 102.67, 52.07, 73.58, 63.86, 102.37, 42.94, 59.73, 93.54 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 144 | 160 | 340
lowIncome_peakRed_18.0_12.5 | 73.65, 73.94, 23.2, 54.21, 33.81, 44.41, 71.0, 38.67, 75.34, 97.22, 149.73, 102.0, 110.99, 133.45, 85.29, 42.35, 102.67, 52.07, 73.58, 63.86, 102.37, 42.94, 59.73, 93.54 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 144 | 160 | 270
lowIncome_peakRed_17.0_12.5 | 73.65, 73.94, 23.2, 54.21, 33.81, 44.41, 71.0, 38.67, 75.34, 97.22, 149.73, 102.0, 110.99, 133.45, 85.29, 42.35, 102.67, 52.07, 73.58, 63.86, 102.37, 42.94, 59.73, 93.54 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 153 | 170 | 200
lowIncome_peakRed_16.0_12.5 | 73.65, 73.94, 23.2, 54.21, 33.81, 44.41, 71.0, 38.67, 75.34, 97.22, 149.73, 102.0, 110.99, 133.45, 85.29, 42.35, 102.67, 52.07, 73.58, 63.86, 102.37, 42.94, 59.73, 93.54 | N, N, N, N, N, N, N, N, N, N, L, L, L, L, L, L, S, S, S, S, N, N, N, N | 162 | 180 | 120